## User Guide
Question | Input
Location of the papermill (to determine feasibility of geothermal/solar) | Île-de-France
What is your energy demand annually for heat/steam (MWh/year) | 70000
Is your mill integrated (if they produce pulp, feasibility for biomass) | Yes
if yes, how much do you obtain wood sludge annually (in tonnes) | 20000
Subsidies | ON

## results
Technology | Capex (EUR) | Opex (EUR) | LCOE (EUR/MWh) | TCO2 avoided | Cost of avoidance (EUR/TCO2e) | Payback Period | Notes
Natural Gas Boiler | 8207678.5911 | 86836365.8537 | 67.8886 |  |  |  | (CAPEX is high as certificates of CO2 are getting more expensive)
Hydrogen Boiler (fuel purchased) | 11784896.0699 | 196582658.4083 | 148.834 | 14140 | -400.7196 | -0.10738 | Opex sub. Is needed
Hydrogen Boiler and Alkaline Electrolizer | 36297742.841 | 65242695.1437 | 72.5289 | 14140 | -22.9717 | 1.6809 | Opex subsidies is needed, Green Hydrogen Tenders France 2030, highly competitive
Electric Boiler | 3405446.1512 | 147368421.0526 | 107.6956 | 14140 | -197.0644 | -0.056259 | Opex subsidies is needed but not offered since 2022 after the UR war, no targeted subsidy but could fit under DECARB IND 25, which offers subsidies on CAPEX, if boiler is part of a more hollistic dcarbonization plan
Biomass | 28557880.4887 | 54779833.8027 | 59.5269 | 11550 | 50.6768 | 0.89086 | Capex subsidies is needed, BCIAT Programe France 2030
Geothermie with heat pump | 4928455.2846 | 52243414.6341 | 127.8081 | 6440 | -651.2992 | 0.14247 | Capex subsidies is needed, Fonds Chaleur, ADEME

## results2
If the Goal is: | The best technology is:
GHG reduction | Hydrogen Boiler (fuel purchased), Hydrogen Boiler and Alkaline Electrolizer, Electric Boiler
Optimal CAPEX | Electric Boiler
Optimal Opex | Geothermie with heat pump
Best LCOE | Biomass
Payback Period | Geothermie with heat pump

## Natural Gas Boiler
Natural Gas
Natural gas LHV | MWh/t | 13.89
boiler efficiency |  | 90%
Natural Gas emission factor | tCO2e/MWh | 0.202 | (IPCC, 2006)
thermal output required | MWh/a | 70000
GHG emissions | tCO2e/a | 14140
natural gas input required (fuel): | MWh/a | 77777.7778
natural gas price | EUR/MWh | 40 | (Europeean comission, Q4, 2024)
annual fuel cost | EUR/a | 3111111.1111
Electricity consumtption | kwh/MWh | 5
estimated lifetime | years | 20
Operating hours | hours | 8200
CAPEX per MW of small boiler of 1 MW | EUR/MW | 700000
CAPEX per MW of big boiler of 100 MW | EUR/MW | 450000
Estimated scalability effect |  | -3623.1884
Boiler Capacity
Adjusted to boiler efficiency | MWh/a | 77777.7778
Boiler capacity | MW | 9.4851
(fraunhofer, 2024)
CAPEX of Boiler
Spec. CAPEX (including of installation) | EUR/MW | 665633.7143
Capacity | MW | 9.4851 | (ADEME, 2024)
CAPEX | EUR | 6313598.9162
Indirect costs | EUR | 1894079.6749
Subsidies | EUR
Total Capex CH-4 Boiler | EUR | 8207678.5911
(Fraunhofer ISE, 2024)
OPEX of Boiler
OPEX (fix) | EUR/MW | 23000
CO2 price of certificate | EUR/t | 70
CO2 price | EUR/a | 989800
| Eur/a | 1207957.1816 | (EU energy, March 2025)
OPEX var. (fuel) | EUR/a | 3111111.1111
Electricity tarif | EUR/MWh | 65
Power demand | MWh/a | 350
OPEX var. (electricity) | EUR/a | 22750
Costs (EUR) | sum
Capex | 8207678.5911
Opex fix | 24159143.6314
Opex var (fuel + electricity) | 62677222.2222
Total costs | 95044044.4447
Production | sum
Energy | 1400000
LCOE of GH4- boiler | EUR/MWh | 67.8886

## Hydrogen+Alkaline Electro
Electrolyser |  |  |  | Hydrogen Boiler
Natural gas | MWh/t | 13.89 |  | boiler efficiency |  | 95%
Hydrogen | MWh/t | 33.33 |  | CAPEX per MW of small boiler of 1 MW | EUR/MW | 1100000
lifetime | a | 20 |  | CAPEX per MW of big boiler of 70 MW | EUR/MW | 400000
Thermal output | MWh/a | 70000 |  | Estimated scalability effect |  | -10144.9275
Mass of hydrogen | t/a | 2100.21 |  | emission factor | TCO2e/MWh | 0
CAPEX per MW of small boiler of 1 MW | EUR/MW | 1200000
CAPEX per MW of big boiler of 100 MW | EUR/MW | 900000 | (IRENA, 2020)
Estimated scalability effect |  | -3030.303
Electrolyer Capacity
Electricity required per tonnes of H2:
Elelctrolyzers (PEM or alkaline) | MWh/t | 64 |  | Boiler Capacity
Total annual electricity demand: | MWh/a | 134413.4413 | (IRENA, 2020, typically consume between 50 to 78 for Alkaline MWh/t of H2, taking 64 as an average) | Adjusted to boiler efficiency | MWh/a | 73684.2105
Annual load | h/a | 8200 |  | Boiler capacity | MW | 8.9859
Electrolyzer capacity | MW | 16.3919
CAPEX of Electrolyzer |  |  |  | CAPEX of Boiler |  |  | (fraunhofer, 2024)
Spec. CAPEX | EUR/MW | 1150327.627 |  | Spec. CAPEX | EUR/MW | 1008838.9053
Capacity | MW | 16.3919 |  | Capacity | MW | 8.9859
CAPEX | EUR | 18856035.9778 |  | CAPEX | EUR | 9065304.6691 | (ADEME, 2024)
Indirect costs | EUR | 5656810.7933 | (IRENA, 2020) | Indirect costs | EUR | 2719591.4007
Subsidies | EUR |  |  | Subsidies | EUR
Total Capex Electrolyzer | EUR | 24512846.7711 |  | Total Capex Boiler | EUR | 11784896.0699
OPEX of Electrolyzer |  |  |  | OPEX of Boiler |  |  | (Fraunhofer, 2024)
OPEX (fix) | EUR/MW | 35000 |  | OPEX (fix) | EUR/MW | 23000
| EUR/a | 573715.9082 | (IRENA, 2020) |  | EUR/a | 206675.2246
OPEX var. (electricity) |  |  |  | OPEX var. (electricity) |  |  | (EU energy, March 2025)
Electricity tarif | EUR/MWh | 65 |  | Electricity tarif | EUR/MWh | 65 | (according to UK BEISS 2022, it is negligeable at around 1% of thermal output annually)
Power demand | MWh/t_H2 | 64 | (EU energy, March 2025) | Power demand | MWh/a | 700
H2 Production | t_H2/a | 2100.21 |  | Total Elect. Cost | EUR/a | 45500
Total Elect. Cost | EUR/a | 8736873.6874
Subsisdies | EUR | -126012601.2601 | (France 2030, ADEME, 3EUR/kg of Hydrogen produced)
Costs (EUR) | sum |  |  | Costs (EUR) | sum
Capex | 24512846.7711 |  |  | Capex | 11784896.0699
Opex fix | 11474318.1635 |  |  | Opex fix | 4133504.4929
Elect Opex var | 174737473.7474 |  |  | Elect Opex var | 910000
Subsidies | -126012601.2601 |  |  | Total costs without fuel | 16828400.5628
Total costs | 84712037.4219 |  |  | Total costs with H2 produced | 101540437.9847 |  | (with H2 purchased from Tunisia at 4.56EUR/Kg)
|  |  |  | Total OPEX with fuel purchased | 196582658.4083
|  |  |  | Total costs with H2 purchased | 208367554.4782
Production | sum |  |  | Production | sum
H2 Production in tonnes | 42004.2004 |  |  | Energy | 1400000
LCOH | EUR/t | 2016.7516 |  | LCOE (with H2 produced) | EUR/MWh | 72.5289
| EUR/Kg | 2.0168 |  | LCOE (with H2 purchased) | EUR/MWh | 148.834
|  |  |  | TCO2e avoided | TCO2e | 14140
Eligibility Criteria for Subsidies: Projects must be located in France Hydrogen production via water electrolysis For renewable hydrogen: electricity must be from renewable sources For low-carbon hydrogen: emissions ≤ 3.38 kg CO₂e/kg H₂ At least 60% of hydrogen production must be secured through commercial commitments Financial guarantee: 8% of the maximum aid requested Compliance with cybersecurity and EU origin requirements​ |  |  |  | Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202
|  |  |  | LCOE natural gaz | EUR/ | 67.8886
|  |  |  | Cost avoidance if H2 Purchased | €/TCo2 | -400.7196
|  |  |  | Cost of avoidance if H2 produced | €/TCo3 | -22.9717

## Biomass
Biomass Boilers for Non-Integrated Paper Mill |  |  |  | Biomass Boilers for Integrated Paper Mill
wood sludge LHV (high quality) | MWh/t | 5 | (AEBIOM, 2022) | wood sludge LHV (high quality) | MWh/t | 5 | (AEBIOM, 2022)
boiler efficiency |  | 80% |  | residual fuel LHV (from pulp) | MWh/t | 1.7
emission factor | tCO2e/MWh | 0.037 |  | boiler efficiency |  | 80%
thermal output required | MWh/a | 70000 | (IPCC, 2006) | emission factor | tCO2e/MWh | 0.037 | (IPCC, 2006)
GHG emissions | tCO2e/a | 2590 |  | thermal output required | MWh/a | 70000
Electricity consumtption | kwh/MWh | 10 |  | GHG emissions | tCO2e/a | 2590
estimated lifetime | years | 20 |  | Electricity consumtption | kwh/MWh | 10 | (ERPI, 2018)
Operating hours | hours | 8200 |  | estimated lifetime | years | 20
CAPEX per MW of small boiler of 1 MW | EUR/MW | 3500000 |  | Operating hours | hours | 8200
CAPEX per MW of big boiler of 70 MW | EUR/MW | 2500000 |  | CAPEX per MW of small boiler of 1 MW | EUR/MW | 3500000
Estimated scalability effect |  | -14492.7536 |  | CAPEX per MW of big boiler of 70 MW | EUR/MW | 2500000 | (Fraunhofer ISE, 2023)
|  |  |  | Estimated scalability effect |  | -14492.7536 | (CE Delft, Danish Energy Agency, 2020)
Fuel Input | MWh/a | 87500 | (ERPI, 2018) | Fuel Input | MWh/a | 87500
Mass of Biomass Fuel needed | t/a | 17500 |  | Mass of Fuel needed (high quality) | t/a | 17500
fuel price | EUR/t | 90 |  | Mass that can be replaced | t/a | 3500
annual fuel cost | EUR/a | 1575000 |  | Equivalence in residual | t/a | 10294.1176 | (from mathias)
|  |  |  | Mass of Residuals Fuel produced | t/a | 20000
|  |  |  | Mass of Residual Fuel sold | t/a | 9705.8824 | (from questionnaire)
|  |  |  | Cost of selling biomass to recycling | EUR/t | 30
|  |  |  | Mass of Wood sludge bought | t/a | 14000
|  |  |  | Residual fuel price (high quality) | EUR/t | 90
|  |  |  | Annual fuel cost | EUR/a | 1551176.4706
Boiler Capacity |  |  |  | Boiler Capacity
Adjusted to boiler efficiency | MWh/a | 87500 | (ADEME, 2022) | Adjusted to boiler efficiency | MWh/a | 87500
Boiler capacity | MW | 10.6707 |  | Boiler capacity | MW | 10.6707
(ADEME, 2022)
CAPEX of Boiler |  |  |  | CAPEX of Boiler
Spec. CAPEX (including of installation) | EUR/MW | 3345351.7144 |  | Spec. CAPEX (including of installation) | EUR/MW | 3345351.7144
Capacity | MW | 10.6707 |  | Capacity | MW | 10.6707
CAPEX | EUR | 35697350.6108 |  | CAPEX | EUR | 35697350.6108
Indirect costs (30%) | EUR | 10709205.1833 |  | Indirect costs (30%) | EUR | 10709205.1833
Subsidies | EUR | -17848675.3054 | (50% on incestment cost, BCIAT Program, ADEME, France 2030) | Subsidies | EUR | -17848675.3054 | (50% on incestment cost, BCIAT Program, ADEME, France 2030)
Total Capex Solid Biomass Boiler | EUR | 28557880.4887 |  | Total Capex Solid Biomass Boiler | EUR | 28557880.4887
OPEX of Boiler |  |  |  | OPEX of Boiler
OPEX (fix) | EUR/a | 1142315.2195 |  | OPEX (fix) | EUR/a | 1142315.2195
OPEX var. (fuel) | EUR/a | 1575000 |  | OPEX var. (fuel) | EUR/a | 1551176.4706
OPEX var. (electricity) |  |  |  | OPEX var. (electricity)
Electricity tarif | EUR/MWh | 65 |  | Electricity tarif | EUR/MWh | 65
Power demand | MWh/a | 700 | (ADEME, 2024) | Power demand | MWh/a | 700 | (ADEME, 2024)
Total Elect. Cost | EUR/a | 45500 |  | Total Elect. Cost | EUR/a | 45500
Costs (EUR) | sum |  |  | Costs (EUR) | sum
Capex | 28557880.4887 |  |  | Capex | 28557880.4887
Opex fix | 22846304.3909 |  | (Fraunhofer ISE, 2024, according to Fraunhofer, take it as a 4% on CAPEX) | Opex fix | 22846304.3909 |  | (Fraunhofer ISE, 2024, according to Fraunhofer, take it as a 4% on CAPEX)
Opex var (fuel + electricity) | 32410000 |  |  | Opex var (fuel + electricity) | 31933529.4118
Total costs | 83814184.8796 |  |  | Total costs | 83337714.2914
|  |  | (EU energy, March 2025) |  |  |  | (EU energy, March 2025)
Production | sum |  |  | Production | sum
Energy | 1400000 |  |  | Energy | 1400000
LCOE of biomass boiler | EUR/MWh | 59.8673 |  | LCOE of biomass boiler | EUR/MWh | 59.5269
TCO2e avoided | TCO2e | 11550 |  | TCO2e avoided | TCO2e | 11550
Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202 |  | Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202
LCOE natural gaz | EUR/ | 67.8886 |  | LCOE natural gaz | EUR/ | 67.8886
Cost avoidance | €/TCo2 | 48.6141 |  | Cost avoidance | €/TCo2 | 50.6768
Eligibility Criteria for Subsidies: Projects must have a minimum annual heat production of 12 GWh.​ Eligible sectors include: Manufacturing sectors as defined by the French national classification (NAF codes). Acceptable biomass fuels include: Forest chips and similar materials. By-products and residues from the primary wood processing industry. End-of-life wood and wood waste. Pellets and other industrial or agricultural by-products.​ res-legal.eu Projects must be part of a comprehensive energy optimization strategy, considering: Energy sobriety and efficiency measures. Recovery of waste heat. Potential integration of other renewable energy sources (e.g., geothermal, solar thermal).​

## Geothermal
Middle geotermal source |  |  |  | High geotermal source
[8 empty] | Fixed investment (€) | 6000000
Natural gas demand | MWh/a | 70000 |  | Natural gas demand | MWh/a | 70000 |  | Water flow (kg/s) | 50
Efficiency | COP | 2.8 |  | Efficiency | COP | 4 |  | Retruned temperature (°C) | 30
Electricity needed | MWh/a | 25000 |  | Electricity needed | MWh/a | 17500
Time of use | hours | 8200 |  | Time of use | hours | 8200 |  | Source Temperature (°C) | ΔT (°C) | Power output (kW) | Specific capex (€/kW)
Capacity of HEAT PUMP | MW | 3.0488 |  | Capacity of HEAT PUMP | MW | 2.1341 |  | 50 | 20 | 4180 | 1435.4067
[8 empty] | 60 | 30 | 6270 | 956.9378
CAPEX |  | 8439024.3902 |  | CAPEX |  | 7040650.4065 |  | 70 | 40 | 8360 | 717.7033
CAPEX with Subsidies |  | 5907317.0732 |  | CAPEX with Subsidies |  | 4928455.2846 |  | 80 | 50 | 10450 | 574.1627
Specific CAPEX | €/MW | 800000 |  | Specific CAPEX | €/MW | 800000 |  | 90 | 60 | 12540 | 478.4689
CAPEX HEAT PUMP |  | 2439024.3902 |  | CAPEX HEAT PUMP |  | 1707317.0732 |  | 100 | 70 | 14630 | 410.1162
Capacity |  | 3.0488 |  | Capacity |  | 2.1341 |  | 110 | 80 | 16720 | 358.8517
CAPEX GEO | €/KW | 956.9378 |  | CAPEX GEO | €/KW | 318.9793 |  | 120 | 90 | 18810 | 318.9793
CAPEX GEO TOTAL | € | 6000000 |  | CAPEX GEO TOTAL |  | 5333333.3333
Subsidies | € | -2531707.3171 | (Fonds Chaleur, up to 65% for social housing, estimated at 30% average for industrial) | Subsidies | € | -2112195.122 | (Fonds Chaleur, up to 65% for social housing, estimated at 30% average for industrial)
Thermic capacity of water = 4.18 kJ/kg·K
OPEX |  | 2612170.7317 |  | OPEX |  | 1990219.5122
Fixed Opex | €(% of capex) | 73170.7317 |  | Fixed Opex | €(% of capex) | 51219.5122
Cost of Electricity | €/MWh | 80 |  | Cost of Electricity | €/MWh | 80
Cost of Electricity/a | €/MWh | 2000000 |  | Cost of Electricity/a | €/MWh | 1400000
CO2 price of certificate | EUR/t | 70 |  | CO2 price of certificate | EUR/t | 70
CO2 price | EUR/a | 539000 |  | CO2 price | EUR/a | 539000
Total cost of use |  |  |  | Total cost of use
Total CAPEX | € | 5907317.0732 |  | Total CAPEX | € | 4928455.2846
Total OPEX (lifetime) | € | 52243414.6341 |  | Total OPEX (lifetime) | € | 39804390.2439
Total cost | € | 58150731.7073 |  | Total cost | € | 44732845.5285
Lifetime | years | 20 |  | Lifetime | years | 20 |  | 0.134
Total MWh lifetime | Mwh | 500000 |  | Total MWh lifetime | Mwh | 350000
LCOE |  | 116.3015 |  | LCOE |  | 127.8081
emission factor of Heat pump + geo | TCo2/MWh | 0.11 |  | emission factor of Heat pump + geo | TCo2/MWh | 0.11
TCO2e emmitted | TCO2e/a | 7700 |  | TCO2e emmitted | TCO2e/a | 7700
TCO2e avoided | TCO2e | 6440 |  | TCO2e avoided | TCO2e | 6440
Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202 |  | Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202
LCOE natural gaz | EUR/ | 67.8886 |  | LCOE natural gaz | EUR/ | 67.8886
Cost avoidance | €/TCo2 | -526.2267 |  | Cost avoidance | €/TCo2 | -651.2992
Eligibility Criteria for Subsidies: Installation of geothermal systems utilizing heat pumps for heating purposes. Applicable to collective housing, agriculture, industry, and the tertiary sector (e.g., commercial buildings). Technical Requirements: Use of certified equipment and adherence to recognized technical standards. Engagement of professionals with RGE (Reconnu Garant de l’Environnement) certification for installation and maintenance. Implementation of monitoring systems post-installation to ensure performance

## Electric Boiler
Electric Boiler
Thermal output | MWh/a | 70000
Efficiency |  | 95%
Electricity needed | MWh/a | 73684.2105
Time of use | hours | 8200
Capacity of boiler | MW | 8.9859
CAPEX per MW of small boiler of 1 MW | EUR/MW | 400000 | https://energy.nl/wp-content/uploads/electric-industrial-boiler-7.pdf
CAPEX per MW of big boiler of 70 MW | EUR/MW | 100000
Estimated scalability effect |  | -4347.8261
CAPEX |  |  | We assume a cost per MW of capacity wich varies (linear) between 100 000€ to 400 000€/MW depending the capacity (from 70 to 1MW) | number of investment year | 2
Specific CAPEX | €/MW | 360930.9594
CAPEX |  | 4864923.0731 |  | interest rate | 1.02
Integration factor (grid connection and integration) | coefficient | 1.5
Integration cost | € | 0
Capacity |  | 8.9859
Subsidies | € | -1459476.9219
CAPEX after subsidies | € | 3405446.1512
OPEX
Fixed Opex | €/MWh | 5
Cost of Electricity | €/MWh | 75
Grid Charges | €/MWh | 20
Other Charges | €/MWh | 0
Total cost of use
Total CAPEX | € | 3405446.1512
Total OPEX (lifetime) | € | 147368421.0526
Total cost | € | 150773867.2038
OPEX per year | € | 7368421.0526
Lifetime | years | 20
Total MWh lifetime | Mwh | 1400000
LCOE |  | 107.6956
Non green electricity | Mwh | 0
Tons Co2 produce per MWh | TCo2/Mwh | 0
Total tons of Co2 produce | TCo2 | 0
Tons Co2 produce per MWh for natural gaz | TCo2/MWh | 0.202
LCOE natural gaz | EUR/ | 67.8886
Cost avoidance | €/TCo2 | -197.0644
Eligibility Criteria for Subsidies: GHG Emission Reduction: Achieve a reduction of at least 1,000 tCO₂eq/year at constant production levels. Minimum Investment: Total investment must exceed €3 million. Aid Request Limit: Funding request should be less than €30 million. Project Location: Must be situated in mainland France or overseas territories. Project Maturity: Solutions should be ready for industrial deployment. Decarbonization Roadmap: Applicants must have a clear strategy for decarbonizing their site by 2030 and 2050

## Heat pump fed by DE-modif
Thermal Output | MWh/a | 70000
Efficiency | COP | 2
Electricity needed | MWh/a | 35000
Time of use | hours | 8200
Capacity of HEAT PUMP | MW | 4.2683
CAPEX |  | 3414634.1463
Specific CAPEX | €/MW | 800000
CAPEX |  | 3414634.1463
Capacity |  | 4.2683
Subvention | € | 0
OPEX |  | 2727439.0244
Fixed Opex | €(% of capex) | 102439.0244
Cost of Electricity | €/MWh | 75
Cost of Electricity/a | €/MWh | 2625000
Total cost of use
Total CAPEX | € | 3414634.1463
Total OPEX (lifetime) | € | 54548780.4878
Total cost | € | 57963414.6341
OPEX per year | €
Lifetime | years | 20
Total MWh lifetime | Mwh | 700000
LCOE |  | 82.8049
Non green electricity | Mwh
Tons Co2 produce per MWh | TCo2/Mwh
Total tons of Co2 produce | TCo2
Tons Co2 produce per MWh for natural gaz | TCo2
LCOE natural gaz | EUR/
Cost avoidance | €/TCo2

## Solar
1 |  |  |  | resources
thermal output needed | MWh/a | 50000 |  | https://task64.iea-shc.org/Data/Sites/1/publications/IEA-SHC-Task64-SubtaskE-D.E2-D.E3.pdf
Yearly in-plane irradiation | kWh/m²/year | 1500 |  | PVGIS https://re.jrc.ec.europa.eu/pvg_tools/en/ | https://librairie.ademe.fr/ged/9529/guide-tout-comprendre-solaire-thermique.pdf (solar irrandiance)
Solar Irradiance | kWh/m²/day | 4.1096
Slope angle [°] | [°] | 35 | take mid of France as example
system efficiency | % | 80%
Annual equivalent full-load hours | h/year | 2400 |  | 1.08
Adjusted to efficiency | MWh/a | 62500
Capacity | MW | 26.0417
Panel Power | MW | 0.00045 |  | https://www.firstsolar.com/-/media/First-Solar/Technical-Documents/Series-6-Plus/Series-6-Plus-Bifacial-Datasheet---Global.ashx?la=en-Emea
| kw | 0.45
Panel Area (size) | m² | 2.5 | based on the 450w production: 2009mm*1232mm=2.47m^2 (34kg) | https://www.firstsolar.com/-/media/First-Solar/Technical-Documents/Series-6-Datasheets/Series-6-Datasheet.ashx?la=en-Emea
panels required | unit | 57870.3704
Required Panel Area | m² | 289351.8519
Land utilization rate (including spacing) | m²/kWp | 5
Required Land Area | m² | 289351.8519
Efficiency Factor | % | 20%
Energy Output | MWh/year | 12500
2
|  | land install | roof install
CAPEX
Photovoltaic system capacity | MW | 62.5 | 62.5 | target energy 50,000 MWh/year ÷ (1,500 kWh/m²×0.8)
Specific CAPEX | €/W | 0.8 | 0.8 | land :>10 MW ; roof：>500 kWc -0.8 €/W | photovoltaique.info/fr/preparer-un-projet/quel-modele-economique/connaitre-les-couts-et-evaluer-la-rentabilite/couts-dinvestissement/
toal CAPEX | € | 50000000 | 50000000
Grid connection factor |  | 1.1 | 1.05 | https://www.rte-france.com/
Grid connection cost | € | 5000000 | 2500000
Subsidy | €
OPEX
Fixed Opex | €/MWh | 15 | 10
Lease | €/year | 231481.4815 | 2893518.5185 | https://www.laregion.fr/ ADEME
Grid Charges | €/MWh | 2 | 1.5 | https://www.rte-france.com/
Other Charges | €/MWh | 1 | 0.5 | Ground including environmental impact assessment
lifetime | year | 20 | 20
total OPEX | € | 22629629.6296 | 69870370.3704
system cost:
total CAPEX（grid connection included） | € | 55000000 | 52500000
Total Cost | € | 77629629.6296 | 122370370.3704
LCOE(no subsidy) | €/kWh | 77.6296 | 122.3704